Engineering Requirements

Earthing

# general requirements

## Facility Earthing Grid

A facility earthing grid shall be provided in accordance with the ENA-EG1 Substation Earthing Guide.

All metallic structural work shall be bonded to the earthing grid.

The inground earth mat shall be installed to permit a representative number of buried conductors and grid joints to be easily exposed for visual inspection as recommended by the ENA-EG1 Substation Earthing Guide.

The earthing grid design shall consider:

- the nature of the environmental conditions especially with respect to the effect of soil pH on the earthing medium.

- actual earth resistivity as measured by the Contractor.

- all metallic objects including pipes, structural steel and fences and their effect on step and touch potentials.

The inground earthing system shall be such that it does not cause galvanic corrosion of in ground metallic structures including but not limited to structures such as metallic pipework and tanks.

Where the facility is connected to a switchyard with an earthing grid of dissimilar metal to that in the facility there shall be galvanic isolation between the facility earthing grid and the switchyard earthing grid.

Detailed calculations and design information shall be submitted for review by the Principal after contract award.

Prior to energising the Contractor shall test the complete earthing system to verify that personnel will not be exposed to hazardous voltages. The Contractor’s tests shall measure the possible step, touch and transfer voltage hazard locations associated with metalwork in or adjacent to an earthing system to ensure safety for power authority personnel and the public. The test results shall be compiled and submitted to the Principal in a preliminary report within one week of the tests being carried out.

## Local Earthing Systems

In areas remote from the facility earthing grid, local earthing systems shall be provided, in accordance with the ENA-EG1 Substation Earthing Guide and AS/NZS 3000. All adjacent metallic structural work shall be bonded to such local earthing systems. The total earth resistance of any such local earthing installation to the general mass of earth shall not exceed one ohm. The Contractor shall prove the effectiveness of the local earthing grid by means of primary current injection with results to be submitted to the Owner for approval.

## Electrical Equipment Earthing

The Contractor shall provide Electrical Equipment Earthing as specified in this clause and as required by AS/NZS 3000. All electrical components, devices and apparatus having a metallic enclosure or framework which may become directly connected to electricity supply following breakdown of insulation, shall be provided with means of attaching earthing conductors.

For assemblies containing several such components or devices, a copper earth bar shall be provided within the assembly to which all devices and enclosures shall be individually earthed. . With the exception of extra low voltage signal cabling, cable earths shall be connected directly to an earth bar. In these cases rail mounted protective earth terminals shall not be used. One conductor per earth bar screw or stud shall be allowed. The earth bar shall also be drilled to accommodate connection back to the facility earthing grid.

All earth bars and cabling which do not come in contact with soil shall be constructed of copper. Any earth cabling, strap and the like which is likely to be in contact with soil at any time shall be constructed of the same material as the buried earth grid so as to avoid the setting up of any electrolytic cell.

Where electrical equipment is mounted on hinged doors or panels, additional means of earthing shall be connected across the hinge points.

All metallic gland plates and metallic components on non metallic enclosures shall have an earth connection.

All earthing connections shall be sized in accordance with AS/NZS 3000 and consist of green/yellow single PVC insulated stranded copper cable. The use of conductors identified by the colours green or yellow either separately or in combination, for any purpose other than earthing is prohibited.

## Earthing of Cable Ladder/Trays

Any cable ladder or cable tray that contains HV cable/s shall be earthed at all joints using earthing bonds separate to the ladder/tray section joints in each of the ladder/tray sections to ensure that the entire ladder/tray is electrically continuous.

The cable tray shall be earthed to the station earth bar via 120mm² copper conductor.

## Instrument Earthing

The following shall be subject to review by the Principal as part of the detailed design reviews under the Contract:

The instrument earth is required to provide a common zero voltage reference point for all instrument and control systems throughout the plant and to minimise internally and externally generated electrical noise and its effect on instrument and control systems.

All control and instrumentation enclosures are to be provided with an instrument earth bus. The bus must be insulated from the enclosure metalwork. The instrument earth bus may be extended from enclosure to enclosure by series or radial connection using insulated conductors and shall be connected to the main instrument earth also by means of a single insulated conductor. The main instrument earth for any whole control system shall be connected to the main electrical earth at one point.

To accommodate a large number of enclosures several instrument earth buses may be used. In this case the system shall be configured so that the earth buses are connected radially to the main instrument earth. No connections are to be made between the radial arms of the system which would create an earth loop.

Electronic analogue input and output signals shall be earthed at one point only (generally through the power supply). Self powered instrument loops shall require an earth connection to be made at one point, preferably at the dc source.

Where earthing of wires, screens etc. is performed at one end only of a cable, then the wires, screens etc. at the end of the cable remote from the earthing shall be appropriately insulated to remove any risk from contacting these remote bare conductors.

Transmitters used in conjunction with primary elements which have an electrical connection with plant steelwork or a process fluid (e.g. thermocouples with grounded hot junction) shall require input/output isolation.

# Lightning Protection

## Standards

All lightning protection systems shall be designed to meet all the requirements of AS/NZS 1768.

## PLC I/O and Instrument Supplies

Comprehensive lightning surge control shall be supplied for all low voltage and instrument cabling entering or leaving an outside facility and outside installations entering the main building.

In particular, all 4 – 20mA instrument loops shall be provided with arrestors at the instrument, converter and the control system terminals. The arrestor shall be a self-resetting single-phase 20kA unit with a clamp voltage of not in excess of 36V with a maximum line current of 1500mA rms.

All 24VDC, status and indication circuits shall be fitted with arrestors at the field device and at the switchboard terminals. The arrestor shall be suitable for balanced and non-balanced circuits, a surge current up to 10kA and a clamp voltage of not in excess of 36V.

# Substation Requirements

## Design of Earthing System

The substation earthing system shall be designed in accordance with the requirements of the ENA EG1 Substation Earthing Guide, AS 2067, IEEE Std 80, AS 3000 and other relevant Australian Standards.

The Contractor shall carry out site tests of the earth resistivity and shall perform calculations to determine the substation earth resistance, step and touch voltages.

The Contractor shall submit the earth grid design and calculations to the Principal for review.

The “as built” value of the substation earth resistance shall be confirmed by means of primary injection prior to bonding to the other earthing systems.

## Joints and Connection to Equipment

Connection to equipment may be bolted or, in the case of stranded conductors, clamped by means of cable connectors.

All joints and connections which are buried and all joints in the earth grid shall be brazed or welded.

The overhead earthwires shall be connected to the earth grid using earthing conductors capable of carrying the maximum earth fault current.

## Portable Earthing

Fixed earthing connectors for use with portable earthing devices specified below shall be provided on each busbar at maximum 30 metres intervals. A rigid earthing loop shall be provided adjacent to each busbar earthing connector. The earthing loop shall be connected to a branch of the earth grid and marked green.

Two sets of portable earthing devices shall be provided. Each portable earthing device shall have:

- An earth end clamp for connection to the earthing loops specified above.

- A line end clamp for connection to the fixed earthing connectors.

- A flexible conductor with clear PVC sheath rated for the substation design fault level, or a minimum of 25kA, for 3 seconds.

A telescopic operating pole of glass fibre or similar material shall be provided for each set of portable earthing devices. The pole shall be of sufficient length to reach the height of connections to the high voltage equipment from ground but retractable into a carrying length not exceeding 2.5m. The pole shall have non-slip hand grips.

For each HV earthing switch means shall be provided to attach portable earthing devices to the phase conductors and to the support structure.

## Substation Lightning Protection

Earth masts and/or overhead earth wires shall be installed to provide lightning protection in accordance with the requirements of AS 1768.

The lightning protection should ensure that all plant and structures within the substation are fully within the protected zones as defined by the “Rolling Sphere” technique.

The Contractor shall submit the design of the lightning protection system to the Principal for review.

## Substation Insulation Coordination

The Contractor shall carry out an insulation co-ordination study to confirm the selection of Lightning Impulse Withstand Level (LIWL) for the equipment specified, and to confirm the location and rating of surge diverters.

The parameters to be used in undertaking the study shall be agreed with the Principal prior to commencing the study.

Any additional surge diverters or changes to LIWL rating of equipment, required to provide adequate insulation co-ordination shall be included within the scope of the contract.

# Review

Standard Engineering Requirements are to be reviewed every five years or prior to issue with any detailed specification which ever is the earliest. The review is to be coordinated by the Manager of Strategic Operational Services.

Return To Top