Engineering Requirements

Noise and Vibration

# introduction

This document only defines the minimum technical requirements.  The Contractor is responsible to meet the guaranteed requirements, including provision of required equipment.

# legislative requirements, codes and standards

The design, manufacture and operation of all items of plant, equipment and machinery supplied under this Contract shall comply with:

- all relevant legislative requirements applying in the State in which the project site is located, for example in Queensland: Workplace Health and Safety Act (2011) and Regulation (2011), Environmental Protection Act (1994) and Regulation (2019),

- all relevant Workplace Health and Safety Codes of Practice and Advisory Standards applying in the State in which the project site is located, for example in Queensland: Managing risks and plant in the workplace Code of Practice 2021, Environmental Protection (Noise) Policy 2019,

- Model Code of Practice: Managing noise and preventing hearing loss at work published by Safe Work Australia,

- the requirements of any Statutory or Local Authority having jurisdiction over the equipment,

- Environmental Noise Guidelines: Wind Farms published by the Government of South Australia (Note: This bullet point is only applicable to the wind farm project),

- such other legislation, standards, codes or guidelines as expressly stipulated by Stanwell as forming part of the Contract, and

- the latest revisions of all relevant Australian Standards, EN Standards, DIN Standards and applicable international standards including, but not limited to, those listed below:

| Code # | Title |
| --- | --- |
| AS 1081 | Measurement of Airborne Noise Emitted by Rotating Electrical Machinery |
| AS 1269 series | Occupational noise management |
| AS 2436 | Guide to Noise Control on Construction, Maintenance and Demolition Sites |
| AS 1055 | Acoustics – Description and measurement of environmental noise |
| ISO 20816 | Mechanical vibration |
| ISO 13373 | Condition monitoring and diagnostics of machines – vibration condition monitoring |
| IEC 60034.14 | Rotating electrical machines - Part 14: Mechanical vibration of certain machines with shaft heights 56 mm and higher - Measurement, evaluation and limits of vibration severity |
| AS 2670 series | Evaluation of human exposure to whole-body vibration |
| AS IEC 61672 series | Electroacoustics – sound level meters |
| IEC 61400-11 (Only applicable to wind farm projects) | Wind Turbine Generator Systems – Part 11: Acoustic Noise Measurement Techniques |

Where more than one standard applies, or equipment is manufactured to standards other than those listed or there is conflict between the Specification and any code, standard or legislative requirement, the more stringent requirement (as determined by the Principal) shall apply.

# noise

## Occupational Noise

The Principal requires all plant, equipment and machinery supplied and/or used by the Contractor to be tested to ensure compliance with this Specification, relevant Workplace Health and Safety legislation and associated Codes of Practice and relevant Australian Standards.

### Permissible Occupational Noise Levels

The primary objective of the contractor shall be to wherever possible eliminate harmful noise emission from plant and equipment and where not possible, reduce noise emission to the lowest practicable level and/or institute noise management and control measures which accord with the ‘hierarchy of control’. This should include noise dampening, where applicable.

The equivalent continuous ‘A’ weighted sound pressure level produced by any machine or group of machines, measured at one metre or more from the machine or group of machines in any location to which a worker can gain access, shall not exceed 85 dBA during normal plant operations, be they continuous, cyclic or intermittent.  The measured equivalent continuous ‘A’ weighted sound pressure level produced by any machine or group of machines, shall be in the environment, location and surrounds of final installation.  For plant which produces higher noise levels during some operating sequences the equivalent continuous ‘A’ weighted sound pressure level based on two occurrences in an 8-hour period shall not exceed 90dBA.  This higher level may only be applied for events, which on average will not occur more frequently than once in 5 days.  The measurement shall be based on the integration of the transient noise events with the normal maximum continuous noise from the plant.

Plant shall operate at less than these specified noise levels for any measurement location at a distance of one metre or greater from the plant item or group of items.

Permissible occupational noise levels must comply with the “Model Code of Practice: Managing noise and preventing hearing loss at work” published by Safe Work Australia.

### Operating Conditions

The plant supplied under the contract shall meet the specified occupational noise levels under any and all operating conditions, and in the location it is installed.  This shall include full or partial loading and any other conditions in which the plant is designed to operate.

### Occupational Noise Testing Procedures

Noise monitoring and surveys shall be conducted by an independent, approved testing authority at the Contractor’s expense.

Test procedures and techniques shall in general comply with the “Model Code of Practice: Managing noise and preventing hearing loss at work” published by Safe Work Australia  and AS 1269.1.

Sound Level Meters used shall conform with AS IEC 61672.1 and shall preferably have an integrating facility for the evaluation of equivalent continuous ‘A’ weighted sound pressure levels.  Field calibration shall be performed in accordance with the appropriate measurement standards or manufacturer’s recommendations.

A copy of the results will be provided by the Contractor to the Principal.

### Allowance for Ambient Noise

The measured levels may be corrected for the contribution of other “background” sound sources.  However, ancillary equipment provided by the Contractor shall not be considered as part of the “background” sound source.

### Corrective Action

If test results exceed the specified noise level, the Contractor shall at his own expense carry out corrective treatment.  Such corrective treatment shall in no way impede proper function of the item, proper ventilation, heat dissipation or reasonable access.

### Unit Enclosure and Acoustic System

If required, an acoustically insulated and “light steel” panelled enclosure shall be provided for the machinery.  The interior of the enclosure and the perforated sheets on the acoustic panelling shall be constructed of hot-dip galvanized steel or carbon steel painted.  Zinc electroplated steel is unacceptable.  Welded areas shall be properly treated to prevent corrosion.

If required, the enclosures shall include a minimum of two silenced ventilation fans designed for and capable of continuous duty to cool the enclosed equipment.  Only one fan shall operate with the other as a back-up.  The enclosure top and sides shall be removable with provisions for lifting for ease of maintenance.  All walkways inside enclosures and those attached to outside of enclosures shall be supplied.  Lighting shall be provided inside the enclosures if required.   The enclosure is to be designed so as not to create a confined space as defined in the relevant legislation.

The acoustic data that shows the expected maximum Sound Pressure Levels (SPL’s) and sound power levels produced by the equipment in operation shall be provided, and shall state the operating mode at which the maximum levels occur and the sound source.  The SPL’s quoted shall be those measured at a distance of 1 meter from the outer housing of the unit using an A-weighted decibel scale, and which is set for the slow meter characteristics.  The 1 metre dimension shall be measured in any direction from the basic outline of the equipment; minor protrusions shall not be considered unless they are sources of noise.

# vibration

This Section sets out methods for measuring vibration severity and for assessing the acceptable vibrations on the following items of plant when it is supplied or installed under this specification/contract:

- rotating machinery;

- pipework and ductwork; and

- structures subject to dynamic loading, including mobile plant.

## Intent

Plant supplied by the contractor shall operate with vibration complying with:

- the Workplace Health and Safety legislation applying in the State in which the project site is located;

- the “Guide to Measuring and Assessing Workplace Exposure to Whole-Body Vibration” and the “Guide to Measuring and Assessing Workplace Exposure to Hand-Arm Vibration” published by Safe Work Australia;

- AS 2670 series - Evaluation of human exposure to whole-body vibration

- the Environmental Protection legislation applying in the State in which the project site is located;  and

- ISO 20816  Mechanical Vibration

Vibration acceptability of plant supplied by the contractor will be evaluated by the following criteria:

- Vibration levels shall be equal to or less than internationally accepted ergonomic and workplace health and safety standards;

- Vibration levels shall not be such as may result in premature failures or accelerated deterioration of plant;

- Vibrations generated shall not adversely affect the surrounding plant or neighbour environments, or adversely affect the life or operation or adjacent plant or machinery.

## Acceptable Limits of Vibration for Rotating Plant

Under no conditions shall the vibration of any plant supplied by the contractor exceed the ‘A’ quality vibration level of ISO20816 for the appropriate plant or machine classification.

This requirement does not preclude the use of regional or industrial standards, however, if the Contractor prefers to use a standard other than ISO 20816 the Contractor shall state the standard to which each item of plant shall be manufactured and the vibration levels, which shall be achieved.  The Contractor shall nominate at least five separate installations where plant of similar size, manufactured to the alternative standard, has been in satisfactory service for more than two years.

The operation of plant supplied by the contractor shall not cause ground vibration that results in a non-compliance with the provisions of the applicable state Environmental Protection legislation.

## Acceptable Limits of Vibration for Non-Rotating Plant

As no standard exists for acceptable vibration levels for non-rotating plant such as structures, each individual case shall be assessed separately by the Contractor.

The assessment shall be based on a determination of dynamic stresses, wear and external effects caused by the vibration.  These and other working stresses shall be related to material properties and a required operating and fatigue life in excess of the minimum project operating life nominated in the “Scope of Work and Functional Requirements” Part of this specification.

Vibration levels of the Non-Rotating Plant and the vibration assessment shall be to the satisfaction of the Principal.

## Measurement

The Contractor shall measure and record the vibrations of the following items:

- all rotating machinery nominated by the Principal;

- pipework and ductwork nominated by the Principal;

- structures nominated by the Principal.

The Principal shall be invited by the Contractor to witness all vibration measurements.  A copy of the measurements shall be given to the Principal.

The Principal may have measurements carried out independently and a copy of these results will be made available to the Contractor.

Should any measurements exceed the allowable, the Contractor shall modify the plant and repeat the measurements.  All modifications and repeat measuring shall be at the Contractor’s expense.

## Vibration Parameters and Methods of Measurement

Measurements shall be carried out in accordance with recognised standards.

For rotating plant, the vibration shall be measured at all bearings in three directions, horizontal, vertical and axial.  All measurements shall be made on surfaces which are rigidly connected and as close as practicable to the bearings.

For machines operating at slow speed where significant vibration occurs above 10 Hz frequency, the vibration shall be measured as the root mean square (RMS) velocity.

For machines operating at speeds below 600 rpm the vibration shall be measured as the time-averaged displacement amplitude.

For non-rotating plant, including structural elements, vibration shall be measured as the displacement mode shape.  Sufficient measurement points shall be chosen, to the satisfaction of the Principal, to define completely the motion of the component in three co-ordinate directions and to discriminate between rigid-body and distortion components.

For non-rotating plant, the time response of the vibration shall also be measured.  If the vibration is at steady state then the time-averaged amplitude (+ and -) and oscillation frequency shall be measured.  If the vibration is transient, peaks shall be measured.

## Instrumentation and Accuracy

Measuring instrumentation shall comply with recognised Standards.

Measurement accuracy shall be within ± 5%.

Instrument calibration certificates shall be furnished and/or field calibration checks described in the test report.

## Operating Conditions for Rotating Plant under Test

Where plant usually operates at a constant speed, vibration measurements shall be made at that speed and under both conditions of no load and full load.  If the results of the no load and full load tests vary by more than 40%, additional plant load tests shall be carried out to the satisfaction of the Principal to define load dependence.

Where plant usually operates over a range of speeds the plant shall have vibration measurements made on it at no load and full load and shall have its load dependence checked as for plant which usually operates at a constant speed.  In addition, the plant shall have vibration measurements made on it over a range of speeds, to the satisfaction of the Principal, to prove the absence of any resonance behaviour.

## Test Conditions for Non-Rotating Plant

Test conditions under which vibration measurements are to be carried out on non-rotating plant will be stipulated by the Principal.  Generally, the tests will be made at usual operating conditions and where appropriate a resonance search will be required.

## Test Report

Vibration measurements shall be recorded and included in a test report.  The report of the plant in its final installed condition shall be included in the final Operating and Maintenance Manuals.  This record shall include the following:

- Contract reference;

- Drawing or plant diagram showing measuring positions;

- Statement of operating conditions;

- Instrumentation used including characteristics such as band width and time constants together with manner of calibration and measurement accuracy;

- Test results (units to be indicated).

# review

Standard Engineering Requirements are to be reviewed every five years or prior to issue with any detailed specification which ever is the earliest.  The review is to be coordinated by the Manager of Strategic Operational Services.

Return To Top